{"text_format":"3","workbook":"xlsx","n_sheets":3,"sheets":["Sheet1","Sheet2","Sheet3"],"read":"whole","date_system":"1900"}

{"sheet":"Sheet1","index":0,"n_rows":7,"n_cols":8,"rows_kept":7,"merged":[[0,0,0,7],[3,0,3,5],[4,0,4,5],[5,0,5,7],[6,0,6,3],[6,4,6,5],[6,6,6,7]]}
["雅安市西康记忆生态文旅街区项目一号地块柴油发电机组报价单"]
["序号","名称","规格","单位","暂估数量","不含税单价（元）","不含税总价（元）","备注（品牌）"]
[1,"柴油发电机组\n500KW\n（备550KW）\n\n\n\n品牌：上柴、潍柴、玉柴等（或等同于以上品牌）","1.配置按设计要求;2.接线端子材质、规格:详见设计要求;3.干燥要求: 满足设计及规范要求;4.含降噪音系统、油管、油罐及排烟、除尘等成套配置，含减振装置;5.满足环保部门规范要求;6.箱体接地，盘柜防火封堵，基础槽钢制作、安装、除锈、刷油，焊、压接线端子;7.发电机房在机组安装时应做柴油发电机房的进出风道。其排烟管应高出屋面并符合当地环保部门的要求。排烟系统应加设防尘，消烟装置。厂商配套提供的储油箱应密闭，且应设置通向室外的通气管，通气管应设置带阻火器的呼吸阀。油箱的下部应设置防止油品流散的设施:8.尾气经烟管经保温处理后排放到屋顶，需设置竖井内烟道，烟道材质、规格型号，烟道保温等详设计;9.其它:满足施工图设计要求及施工验收规范要求。","套",1]
["税金（税率     %）"]
["含税合计金额"]
["注：1、报价为综合包干单价，包含含发电机、发动机、发电机随机带的电控柜、自启动控制系统、储油箱(满箱油)、消声器、烟尘处理、油烟净化器、出线开关、设备的生产出厂费、包装费、运输及吊装定位费、安装调试、技术服务费、维修保养费及油耗材料费、排烟除尘费\n2、报价注明品牌、烟道配套长度，以及超过配套长度后不含税单价"]
["报价单位：",{"$nulls":3},"报价人：",null,"联系电话："]

{"sheet":"Sheet2","index":1,"n_rows":0,"n_cols":0,"rows_kept":0}

{"sheet":"Sheet3","index":2,"n_rows":0,"n_cols":0,"rows_kept":0}